## Slide 1: Clearfield (PA) Conveyance System Modeling and Monitoring Project
PennTec 2014
State College, PA
June 3, 2014
Presented By:
Gwin, Dobson & Foreman, Inc.
Altoona, PA

## Slide 2: Presentation Outline
Inflow/Infiltration Source Removal, Convey /Treat or Both?
Clearfield Case Study
  System Description – Overflow Problems
  Original I/I Removal Project – Replace Total System
  DEP Consent Order & Agreement
  Post Construction Monitoring & Modeling
  Treatment & Conveyance System Upgrades
Observations/Lessons Learned
Questions

## Slide 3: Important Questions…
For systems with high wet weather flows, is the best strategy…
  I/I source removal?
  I/I conveyance and treatment?
  or combination of the above?
Most systems have some level of inflow and infiltration
True sanitary sewer systems – designed to carry only sanitary waste – bypass or discharges are considered SSOs
Combined systems – designed to carry both sanitary and stormwater – bypasses or discharges are designated CSOs – confined to systems 50 – 100+ years old
SSO and CSO abatement is a regulatory priority

## Slide 4: Important Questions…
System owners and engineers often face the dilemma of removing or treating I/I
This presentation will discuss lessons learned and options to consider when faced with similar situations
Clearfield system will be presented to offer practical problems and insights

## Slide 5: Clearfield Case Study
  Clearfield Municipal Authority (CMA)
    Service Area – 6,000 connections in Clearfield Boro & Lawrence Twp
    Authority owns interceptor sewers network, pump stations and regional treatment facility
    Borough and Township own their respective collection systems
    Older portion designed as combined sewer system with CSO’s
    CMA under Consent Order & Agreement to eliminate overflows
    CMA required to provide Biological Nutrient Removal
Clearfield, PA

## Slide 6
Clearfield
Borough
Wastewater Treatment Facility with Overflow
Lift Sta. No. 1
Overflow
Overflow
Overflow
Lift Sta. No. 2
Lawrence
Township
Lawrence
Township
Lawrence
Township
I-80
US Rt 322
US Rt 322
Rt 879
Rt 879

## Slide 7: Sewer System Description
  Total System - 341,000 LF (65 miles), 6,000 Customers
  Allocated by System Ownership:
  Clearfield Municipal Authority
    85,300 LF (16.5 miles) - interceptor sewers and force mains (25%)
    Five (5) lift stations
    One (1) SSO and three (3) CSOs
    Regional wastewater treatment facility
  Clearfield Borough
    148,000 LF (28 miles) - sewage collection system (43%)
  Lawrence Township
    107,000 LF (20.5 miles) – sewage collection system (32%)

## Slide 8: System Overflows
  In 2004, CMA system maintained 10 overflows
  6 overflows have since been closed
  4 remaining overflows are manually activated during wet weather events to prevent system surcharging and backups
  Overflows consist of a combination of SSO’s in Lawrence Township and CSO’s in Clearfield Borough

## Slide 9: Historical Background
  Regulatory action forced the community to develop an Act 537 wastewater management plan to eliminate overflows in 1995
  Decision makers were faced with either removing I/I to eliminate overflows or expand treatment plant & conveyance system
  Municipalities decided to entirely replace sewer system and laterals; the Clearfield Municipal Authority expressed reservations with the plan advocating conveyance/treatment
  Clearfield Borough spent $30M to replace all sewers & Lawrence Township invested over $10M (thus far) to replace most sewers
  Clearfield Municipal Authority faced with a WWTF expansion & BNR Upgrade and possible conveyance system project ($40 M)

## Slide 10: Municipal Sewer Replacement Project
  From 2001 to 2011, Borough and Township’s projects replaced all main line sewers and the majority of private laterals back to the house foundation
  Project only replaced private laterals when property owners agreed to sign easements
  System inspection of houses for illegal connections was sporadic after construction
  Although infiltration was reduced, peak flows in the system still cause overflows which collectively would far exceed capacity of the treatment plant
  In 2013, PADEP issued a Consent Order & Agreement to remove overflows since sewer project was not successful
  Authority must now expand plant for peak flow and plan for interceptor upgrades if I/I is not removed

## Slide 11: CMA Flow Monitoring Program Elements
Do quantify problem severity, CMA & GDF designed a monitoring program to isolate problem areas and a basis for model calibration
Accurate flow data is critical to prioritize corrective action & structural improvements
Sufficient period of record is needed - monitoring must be conducted at numerous locations for long periods of time to capture wet weather events
Flow meter programmed designed for different hydraulic conditions (surcharge, free flow, reverse flow)
Continuous meter maintenance and weekly data collection
Commitment of budget resources for flow monitoring program is a must; many tasks done by CMA personnel

## Slide 12: Flow Monitoring Devices
  Initial program monitored flows at sixteen (16) strategic locations in the main conveyance lines and CSOs/SSOs
  Total of twenty-seven (27) flow monitoring locations from 2011 to 2014
  Combination of area-velocity and
  flow-tube flow meters

## Slide 13: Flow Monitoring Devices
  Area-Velocity Meters
    Continuous wave Doppler technology measures average velocity
    7 meters installed in non-surcharged areas
    Primarily used in areas not prone to surcharge conditions
  Flow-Tube Meters
    Transducers estimate flow through pressure differential in the upstream and downstream sections of the meter
    3 meters installed in frequently surcharge areas (pressure pipe flow) and in submerged overflow pipes with the potential for reverse flow

## Slide 14: Flow Monitoring Data Collection
  Authority personnel trained on proper operation and maintenance of flow meters
  Weekly downloads of flow meter data
  User friendly interface for quick and efficient data retrieval. Ability to view real-time flow data and identify any real-time problems and make adjustments
  Engineer oversight with Authority for first six (6) months of flow study (November 2011 to May 2012)
  From May 2012, Authority maintains flow meters and downloads and submits data to Engineer for analysis

## Slide 15: WWTF Flow Monitoring Devices
  Existing WWTF flow meters
    WWTF influent low meter: Parshall flume
    WWTF bypass: weir with ultrasonic level transducer
    Both meters record continuous flows on chart recorders at the treatment facility
    Rainfall data recorded and compared with flow data to develop peak flow and total volumes trends relative to precipitation intensity
    Significant precipitation events >0.50 inches in 24-hours
    Major precipitation events resulted from >1.00 inches in 24-hour period or events with high precipitation intensity, i.e.. > 0.50 inches/hour

## Slide 16: Flow Monitoring
  Interceptor sewers are monitored to quantify subsystem dry weather baseline and wet weather flow
  Peak wet weather flows range up to 25 times dry weather flow indicative of significant I/I problems
  Example: Hyde City Lift Station No. 2 (1.50 MGD capacity).
    Normal ADF : 0.29 MGD (separate sanitary sewer system)
    Peak wet weather loading > 3.0 MGD
    To prevent flooding of pump station, flow is diverted to Montgomery Run SSO
    Raw wastewater effluent bypassed to Montgomery Run after course bar screening for solids
    DEP fines are assessed on per calendar day of overflow volume

## Slide 17: Flow Monitoring Results (Post Construction)
  WWTF Plant Capacity: 4.5 MGD
  WWTF ADF: 2.2 MGD
  Peak Wet Weather Hourly Flow: 15 MGD
  Infiltration reduced by 0.5 MGD
  Overflows still occur 10-20 times per year
  Sanitary sewer subsystem at Hyde City regularly discharges in excess 2.5 MGD

## Slide 18: Flow Monitoring Summary (2011-2014)
  Flow Monitoring 2011 –2014
  Total 54 significant precipitation events
    Peak event precipitation: 2.78 inches in 91 hours (0.40 inches/hour max hourly precipitation)
    Max hourly precipitation during an event: 0.77 inches/hour
    30 of 54 metered events caused CSO/SSO overflows
    Peak event CSO/SSO discharge volume: 12.5 million gallons
    Peak CSO/SSO discharge rate: 6.4 MGD
    Peak hourly total flow: 15 MGD
    24 events with peak hourly flow greater than 7 MGD
    15 events with peak hourly flow 10 MGD or greater
              CSO/SSO Events Summary Table
Year | Annual Rainfall | No. of Metered Significant Precipitation Events | No. of CSO/SSO Events | Annual CSO/SSO Volume | Max. Daily CSO/SSO Flow
 | (inches) |  |  | (MG) | (MGD)
2011 | 51.26 | 5 | 18 | 110 | 6.4
2012 | 34.78 | 19 | 12 | 32 | 5.6
2013 | 31.77 | 22 | 10 | 24 | 5.1
2014 (to date)* | 14.7* | 8 | 7* | 7* | 6.0*

## Slide 19
Chart: Hydrographs of Clearfield Municipal Authority January 30-31, 2013 Rain Event

## Slide 20: Conveyance System Modeling
  Model Developed to Confirm Surcharged Locations and for Capacity Design of Future Conveyance System
  Bentley SewerGEMS V8i Software Package
  Facility Components
    Gravity interceptors
    Submerged outfalls
    Pump stations
    Force mains
    Overflows
    Inverted siphons

## Slide 21: Model Input
  Model created from a compilation of as-built drawings and field instrument surveys
  Physical Data
    Pipe materials, lengths, diameters, invert elevations
    Manhole diameters, invert and rim elevations, locations
    Pump station wet well elevations and volumes, pump set-point controls, certified pump discharge curves, pump elevations and pump station mechanical piping and force main
    Siphon box invert and rim elevations, siphon barrel materials, lengths, lengths, elevations
    Overflow configurations

## Slide 22: Model Input Graphics

## Slide 23: Model Calibration
  Model calibrated with flow monitoring data during baseline conditions and wet weather events
  Hydraulic grade line elevations computed from model were compared with actual flow metering levels for various flow rates throughout the system
  Adjustments to the model were made to achieve a tolerance of one to two inches between the differences in HGL between the model output and calibration data

## Slide 24: Model Output and Graphics

## Slide 25: Consequences of Sewer Surcharging
    Majority of main interceptors have insufficient capacity to convey peak flows without surcharging
    Model confirmed that peak flows are greater than gravity flow conveyance capacities at overflows
    Surcharging of sewer lines is not permitted by DEP
    Frequent surcharging of sewer lines results in pipe failure and decreases its effective life span
    Surcharging of main lines may result in backups in private laterals
    The overflows are designated SSO violations since all combined sewers have been separated

## Slide 26: Design of Future Conveyance System
  If ongoing municipal I/I reduction is unsuccessful, CMA mandated to increase capacity of interceptors, lift stations and force mains
  Model was used to design a new main 42” diameter gravity interceptor to the WWTF
  New interceptor sized to convey a future peak flow of 25 MGD to the treatment facility to eliminate all overflows from the system (assuming future I/I is unsuccessful)
  Other future conveyance system upgrades will be programmed to convey all flow to the treatment plant

## Slide 27: Inflow/Infiltration Sources
  Wet weather flows results from ongoing customer connection inflow not removed in the original project and ongoing municipal cross-connections
    Roof leaders
    French drains
    Sump pumps
    Cross connections

## Slide 28: Ongoing System Infiltration/Inflow Work
  DEP has issued a CO&A with fines for SSO discharges
  The municipalities are now undertaking an aggressive private lateral and home inspection program
  Outside inspection agency hired to conduct the home inspections
  However, long term I/I reduction is questionable due to meager municipal resources

## Slide 29: Private System Inspections
House connections (laterals and building sewers) must be the focus
House connections and laterals can account for 40% - 8% of total system wet weather flow (WEF

## Slide 30: House Inspections
Need to inspect for:
  Storm, surface, groundwater and spring connections
  Roof, foundation and floor drains
  Sump pumps
  Industrial/commercial process water
Public support is beneficial:
  Newspaper articles to explain program in detail
  Project Manager s should have good communication & “people” skills
  Respect for homeowners and private property
System rules & regulations, municipal ordinance support and associated fines a must for proper enforcement
Tracking & follow-up inspections needed for compliance
No exceptions – stay firm and treat everyone equally
Public sewer system must also have I/I integrity

## Slide 31: Wastewater Treatment Facility Upgrades

## Slide 32: Wet Weather Options
Historically, wet weather flows in larger, older systems are handled in several ways:
  Bypass wet weather flows in conveyance system upstream of plant
  Combined systems are required to maximize conveyance and treatment in LTCP (Nine Minimum Controls)
  Equalization storage at conveyance system or plant
  Side stream treatment with disinfection only, if allowable
  Depending on process requirements, some plants are capable of treating the full range of flows directly in the process – this was examined for Clearfield plant upgrade

## Slide 33: Wastewater Treatment Facility Upgrades
  Originally built in 1958, the Clearfield wastewater treatment plant is to be upgraded for nutrient removal and expanded to 25 MGD for system wet weather flow
  Process treatment system will utilize a step-feed system to divert wet weather flow around BNR process
  Although replacement projects have been unsuccessful in reducing peak wet weather flows, the Township and Borough are obligated to remove I/I per Consent Order & Agreement
  If Township/Borough I/I efforts fail, further conveyance system work may be needed (including pump station, force main, interceptors) that could total $1 million

## Slide 34: Conveyance Work if I/I Removal is Unsuccessful
  Upgrade main pump station, force main and gravity interceptor to the WWTF to provide conveyance capacity for the wet weather flows
  Following the completion of the project, the Authority will be able to close the SSOs
  Total cost for the WWTF improvements is $35M with wet weather upgrade options estimated at $5M.

## Slide 35
Clearfield Wastewater Treatment Facility Upgrade & Expansion

## Slide 36: Evaluation of Treatment Alternatives
Conducted extensive wastewater characterization influent wastewater over full range of flows
Evaluated existing treatment processes and conducted preliminary screening of various Nutrient Removal Technologies (NRT)
Dynamic process modeling (BioWin) of various NRT processes, simulated wet weather flows for impact
Selected Hybrid Bardenpho with Virginia Initiative Plant option for cold, wet weather flows
  Step feed diluted wet weather flow to last oxic zone to provide secondary (contact stabilization) treatment

## Slide 37: Selected Wet Weather Process - Step Feed
  Diverts wet weather flow to the last process oxic zone
  Provides biological treatment of all diluted wet weather by contact stabilization (1-2 hour detention)
  Preserves BNR process stream (Virginia Initiative Plant process configuration used in cold, wet weather periods)
  Preserves nitrifiers and denitrifiers to maintain nitrogen and phosphorus removal during and after high flow events
  Prevents elevated DO concentrations in BRN process
  More importantly, prevents biomass washout that would otherwise take BNR process weeks to recover.

## Slide 38: BNR Process with Wet-Weather Step-Feed
Step Feed Discharge to Last Oxic Reactor Zone
BNR Process Reactor
BNR Process Reactor
Step Feed Channel
Final Clarifiers (3)
BNR Process Flow Distribution Box

## Slide 39: Clearfield Case Study - Lessons Learned
Original municipal plan to eliminate overflows was for total sewer system replacement
The project was not successful since overflows are ongoing (10-20/year) due to inadequate inspection of house laterals & direct connections
This has resulted in a DEP Consent Order & Agreement and municipalities must undertake further I/I removal through selected projects and house inspections
Failure to eliminate overflows will result in the Clearfield Municipal Authority upgrading pump stations, force mains and interceptors
Ongoing treatment plant work has provision for processing current peak system flow that is incorporated in a BNR process through step-feed
The Authority believes unnecessary costs were incurred when conveyance, treatment and selective I/I diagnostic work would have achieved the same result for less money

## Slide 40: Clearfield Case Study - Lessons Learned
For new systems with surcharging or overflows, I/I removal may be the best option especially when Peak to ADF ratio is less than 5 : 1
However, flow monitoring and I/I diagnostic work is essential to define subarea contributions and facilitate flow isolation
In older systems, communities with dwindling resources for maintenance personnel and equipment may be inadequate for long term I/I control
Total system replacement does not address inflow adequately unless ongoing house inspections and I/I diagnostic work is a long term commitment – difficult for older “cash strapped” communities
In larger older systems, a mix of treatment and conveyance system expansion with targeted I/I removal may be the best option
To incorporate wet-weather flow (> 5 : 1 Peak to ADF in a BNR process, consider a step-feed option in the plant design

## Slide 41: Questions